## Slide 1
POWER IN
HEAT OUT
ASSURANCE AROUND
IT
Data Centres,
Read as Financial Assets
A front-office masterclass: physical chains, commercial packages, price evidence and diligence
Infrastructure M&A | Project finance | Credit | Origination
Evidence base: MASTER_DC_COST_ONTOLOGY v0.1.1 (frozen 2026-10-06) | 418 equipment lines | 16 branches (A to P)
Notes: Welcome. This masterclass has one job. It turns a data centre from a black box with a dollars-per-megawatt number on the side into a physical system you can follow, price sensibly and challenge in diligence. You are not here to become an electrical or mechanical engineer. You are here to build enough physical and commercial fluency to do five things. Follow how power gets from the grid to the rack. Follow how heat gets from the chip to the atmosphere. Understand what sits inside each major system. Understand how that equipment is bought and what price evidence is genuinely valid for it. And connect all of that to replacement cost, bankability and buy-versus-build. The graphic on the right is the whole course in one picture. Power flows in along the amber line. Heat flows out along the teal line. The violet line is everything that makes the asset safe, observable and provable: fire, security, controls, fibre and commissioning. Every slide you are about to see belongs to one of those three lines. A word on evidence. Everything in this deck is anchored to a frozen equipment ontology of 418 lines across 16 branches. That workbook tells us what exists physically, how it is packaged, and, importantly, where public price evidence is strong and where it is still an open gap. Where the deck shows a number, the number is labelled as current or historical, and as a package or a component. Where no defensible current price exists, the deck says so. That honesty is a feature. A banker who knows which numbers are weak is more useful than one who quotes a precise number from the wrong source. Plan roughly two to three hours if you read the notes properly. Move on when you are ready.

## Slide 2
A DATA CENTRE IS THREE CHAINS CONVERGING ON ONE LOAD
Power flows in, heat flows out, and assurance wraps both
POWER
electrical chain
Grid connection
Branch B
HV/MV + transformer
Branch B
Generator + UPS
Branch C D
LV board + busway
Branch E
Rack PDU
Branch E M
THERMAL
heat chain (runs right to left)
Atmosphere
Branch F
Chillers / heat rejection
Branch F
Water or coolant loops
Branch F H
Capture: air or liquid
Branch G H
Server heat
Branch IT load
ASSURANCE
proof and protection
Fire / life safety
Branch I
Security
Branch J
Controls / metering
Branch K
Fibre / white space
Branch L M
Commissioning
Branch O
IT LOAD
servers, GPUs, network
1 MW of IT load means about 1 MW drawn electrically and about 1 MW of heat to reject, all watched by the assurance chain.
Notes: Start with the most useful mental model in the whole course. A data centre is three chains that all meet at one place, the IT load. The amber chain is electrical. Grid power comes in, is protected and stepped down, is backed up by generators and by UPS batteries, and is distributed through low voltage boards and busway to the rack. Read it left to right. The teal chain is thermal. Nearly every watt the servers consume turns into heat. That heat has to be captured at the chip or the rack, moved by air or liquid through loops, and rejected to the atmosphere. Notice the arrows run right to left. Power travels towards the IT load and heat travels away from it. Keep that direction in your head, because it explains why cooling plant is sized to what the IT load draws, and why a power constraint and a cooling constraint can both cap the same megawatt. The violet chain is assurance. Fire protection, security, controls and metering, fibre connectivity, and commissioning. Its cargo is confidence. It is what lets a lender or a customer believe the first two chains will keep working. The small letters under each box are the branch letters in the ontology workbook, A to P. B is grid and HV/MV, C is standby power, D is UPS and stored energy, E is LV distribution, F is heat rejection, G is white-space air cooling, H is liquid cooling, I fire, J security, K controls, L network, M white space, and O is maintenance and commissioning. You will see those letters again. The bottom line is the finance point. A single dollars-per-megawatt number compresses all three chains. When it is wrong, you cannot tell which chain is wrong. Learning the chains lets you decompose it.

## Slide 3
ANY EQUIPMENT ROW CAN BE READ WITH FIVE MOVES
Read the ontology row, then ask the five questions it answers
Ontology ID
D-010
Equipment
VRLA battery string
Branch / system
D UPS and stored energy
Quantity-driver code
QU
Evidence code
P
Lifecycle
Up to 100% of string; interval UNKNOWN
Real row from the frozen workbook. QU is defined there as protected kW + runtime + redundancy.
1
Physical job
What does it do, and what physical thing happens if it is missing?
Stores energy so the load rides through a grid failure until generators start.
2
Quantity driver
What sets how many or how big?
Protected kW, minutes of runtime and redundancy. Not rack count.
3
Commercial package
Is it a line, or a child of something bigger?
May sit inside the UPS price. Conditional, never assumed.
4
Valid evidence
Which source class can price it, and for what date and scope?
OEM quote, tender or award. A retail UPS price is the wrong scale.
5
Risk created
What can go wrong commercially?
Replacement cycle, runtime shortfall, fire-code and warranty exposure.
Four commercial states that are routinely confused:
Included
in the quoted price
Housed
physically inside a module, price may sit elsewhere
Installed
fixed and connected on site
Commissioned
tested under load and accepted
Notes: This is the operating method for the whole deck. Take any row in the ontology workbook and ask five questions. The row on screen is a real one. D-010 is a valve-regulated lead-acid battery string, in branch D, UPS and stored energy. Its quantity-driver code is QU, which the workbook defines as protected kilowatts plus runtime plus redundancy. Its evidence code is P, which only means a primary product family was found when the row was created. It does not mean a current price exists. Its lifecycle entry says up to one hundred percent of the string may need replacement, and the interval is unknown. The workbook deliberately refuses to insert a generic three-to-five year assumption without a source. Move one is the physical job. A battery string stores energy so the load rides through a grid failure until the generators start. Move two is the quantity driver. It is protected load times minutes of runtime, times the redundancy design. Rack count and floor area do not drive it. Move three is the commercial package. The battery may be priced inside the UPS package, or as a separate line. The ontology has frozen rules that make that conditional on vendor scope. You will see that on the UPS package slide. Move four is valid evidence. Which source class can price this, for which date and scope? An OEM quote, a tender or an executed award. A retail price for a ten kilovolt-amp rack UPS is the wrong scale. Move five is risk. For batteries that means replacement cycles, runtime shortfall against what customers were promised, and fire and warranty exposure. Along the bottom are four commercial states people routinely confuse. Included means in the quoted price. Housed means physically inside a module while the price may sit elsewhere. Installed means fixed and connected on site. Commissioned means tested under load and accepted. A lot of double-counting and a lot of overstated capacity come from sliding between these four words. We will keep returning to them.

## Slide 4
THE ONTOLOGY IS LARGE AND PUBLIC PRICE EVIDENCE IS THIN
Of 418 equipment lines, only 10 carry a native public price observation
Chart: 
| A Site / external | B Grid / HV / MV | C Standby power | D UPS / stored energy | E LV distribution | F Heat rejection | G White-space air | H Liquid cooling | I Fire / life safety | J Security | K Controls / BMS | L Network / carrier | M White space | N Plumbing / MEP | O Maint. / commissioning | P Power interfaces
Equipment lines in ontology | 37 | 35 | 32 | 25 | 30 | 31 | 23 | 35 | 28 | 25 | 28 | 20 | 20 | 19 | 23 | 7
Lines with a native public price observation | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 1 | 0 | 0 | 0
Where public prices are strongest
Small and packaged UPS, commodity LV breakers, PLC and control hardware, optical termination, racks, selected test kit.
Where they are weakest
HV switchgear, large transformers, bespoke MV/LV line-ups, hyperscale UPS, central chillers and cooling towers, CRAHs and fan walls, CDUs.
What follows
Visibility falls as equipment becomes project-engineered. The biggest-ticket systems are the ones with the thinnest current public evidence.
CURRENT PRICE GAP
Gaps stay open.
Notes: Before we go into the systems, look at the territory we are mapping. The frozen ontology has four hundred and eighteen equipment lines across sixteen branches. The slate bars are the number of lines in each branch. The amber bars are the number of lines in each branch that carry at least one native public price observation. Ten lines out of four hundred and eighteen. Fifty-nine lines have primary OEM product evidence, which tells you what the equipment is and says nothing about cost. Look at where the amber sits. Controls, network, small UPS, a commodity breaker, a rack. These are catalogue products with posted prices. Now look at where the amber is missing. Grid and HV and MV equipment, heat rejection, white-space air cooling, liquid cooling. Those are the largest-ticket, most engineered systems, and they are sold by quotation. This gap reflects the structure of the market. A better scrape would not remove it. The more a product is configured to a site, a rating and a voltage, the less likely anyone posts a price. For a banker the consequence is direct. The systems that dominate capex are precisely the systems for which you will rely on package evidence, tenders, executed awards and historical cost plans, and you will have to be disciplined about their scope and date. The ontology names this gap explicitly and keeps it open. Current-price gaps remain real for transformers, HV and MV switchgear, large UPS and batteries, LV equipment and busway, central cooling and liquid cooling. This deck will never fill those gaps with an invented number. When you see the red gap badge later on, that is what it is telling you.

## Slide 5
ELECTRICAL CHAIN | GRID TO RACK
A signed grid connection is not rack-level usable capacity
~
Grid connection
MVA firm, N-1
B
Contract is not energisation
HV/MV protection
MVA / kA fault level
B
Protection scheme and who owns the bay
Transformer
MVA, voltage ratio
B
Package may include RMU, metering, bay
G
UPS
Generator + UPS
kW + minutes + N+x
C D
Generator and UPS sold as sub-systems
LV switchboard
Amps, fault rating
E
Board rating caps what the room can use
Busway / PDU
Amps per feed
E
Tap-off design caps real density
Rack PDU
kW per rack, A/B
E M
A and B feeds must be independent
IT load
kW per rack
M
Density may exceed what the path serves
Quantity
driver
Ontology
branch
Commercial
trap
HV or MV, set by the utility connection
Step down
LV (0.4 kV in the EXCOOL plan basis, which steps 22 kV to 0.4 kV)
Voltage
Three different claims about the same megawatt:
Contracted
right on paper
Energised
live and protection-approved
Deliverable to rack
firm through every downstream stage
Notes: This is the spine of the electrical story. Read it left to right: grid connection, HV and MV protection, transformer, generator and UPS, LV switchboard, busway and PDU, rack PDU, and finally the IT load. Each box has a little symbol so you start to recognise the equipment in a single-line diagram. The teal row gives the quantity driver at each stage. This is the single most important habit for a model. At the front of the chain you size in MVA and fault level. At the generator and UPS you size in kilowatts, minutes of runtime and redundancy. At the LV boards and busway you size in amps. At the rack you size in kilowatts per rack. If someone prices every stage in dollars per megawatt, they are hiding four different unit conversions inside one number. The grey row is the ontology branch, B through E, then M for the rack hardware. The red row is the commercial trap that most often appears at that stage. At the front end the trap is treating a contract as energisation. In the middle the trap is that equipment is sold as sub-systems, so the generator package and the UPS package each contain items that also appear as their own lines elsewhere. At the rack end the trap is that a busway tap-off or an A and B feed design can cap usable density below what the rest of the chain could support. The ribbon shows voltage. The step-down happens at the transformer. The reference cost plan we use later in this course steps from twenty-two kilovolts to point four kilovolts. That is one example, and real sites differ with the utility. Finally the three chevrons. Contracted, energised and deliverable to rack are three different claims about the same megawatt. A banker should ask which claim the seller is making, and what evidence sits behind it. A connection agreement is contracted. A utility certificate and a tested protection scheme is energised. Deliverable to rack needs a firm path through every stage you see above.

## Slide 6
ELECTRICAL CHAIN | HV/MV INTERFACE
The substation is a protected corridor, and every symbol is a priced line
~
Utility
HV feed
Surge arrester
B-011
Disconnector +
earth switch
B-004 / B-005
HV circuit
breaker B-003
CT
B-006
VT / CVT
B-007
Protection relay B-008
+ control panel B-018
Substation DC supply
B-019 charger, B-020 battery
Main power transformer B-015, fans B-033, monitor B-032
NER B-017
MV switchgear B-021, coupler B-024
MV breakers B-023, cables B-026, terminations B-027
to MV/LV transformers, UPS blocks, chillers
Simplified single-line diagram: power flows left to right, dashed violet lines are protection signals.
Why this slide matters to a lender
1
Ownership boundary
Who owns the bay, the utility or the operator? It decides capex and who replaces what.
2
Fault level and protection
Wrong settings mean nuisance trips or damaged plant. Needs utility approval.
3
Redundant feeds
Two incoming feeds only help if they are electrically independent.
4
Energisation date
The date power is truly live is a critical path milestone.
CURRENT PRICE GAP
HV switchgear and large transformers are RFQ-heavy with no usable current public price (gap profile GP-B). Use tenders, utility or EPC bills of quantities and executed awards, with scope stated.
Notes: This is a simplified single-line diagram, the engineer's way of drawing a power system. Power enters from the utility on the left and moves right. The line is the conductor. Everything hanging off it is a device that protects, measures or switches it. Walk through it. The surge arrester gives lightning and switching surges a safe path to earth. The disconnector and earth switch let people isolate and ground a section so it can be worked on safely. The circuit breaker is the device that actually interrupts fault current. Fault current is the huge current that flows if something short-circuits. The current transformer and voltage transformer are measurement devices. They shrink the line current and voltage to small signals. Those signals feed the protection relay, which decides in milliseconds whether to trip the breaker. The substation DC battery and charger sit underneath because the protection must still work when AC has failed. The main power transformer steps voltage down. The neutral earthing resistor limits earth fault current so a fault does not destroy equipment. Then the MV switchgear splits power into feeders, with a bus coupler so two sections can be tied together or separated. MV cables carry power to the next stage. Why does a finance audience need this? Because every symbol on this slide is an ontology line, and many are bought as part of a bigger package. A single price for a substation bay can contain breakers, instrument transformers, relays and the control panel. If your model also carries those as separate lines, you have double-counted. Package controls in the ontology say that for a transformer or bay package these children are suppressed only when the vendor scope says they are included. The four points on the right are diligence prompts. Ask who owns the bay. Ask for the protection study and the utility's approval. Ask whether two feeds are truly independent. Ask for the actual energisation date, not the contracted date. On evidence, this is an area with no usable current public price. The ontology records it as a gap and points you to tenders, bills of quantities and awards. Keep it that way in your model until you have project-specific evidence.

## Slide 7
ELECTRICAL CHAIN | TRANSFORMERS
A transformer is quoted by kVA, and the bay around it is where scope hides
Anatomy (simplified)
HV in
LV out
Fans / pumps
B-033
Amber coil: HV winding, more turns. Teal coil: LV winding, fewer turns. The iron core links them. The tank holds insulating liquid that carries heat to the radiators.
Voltage ratio equals turns ratio. Size is kVA or MVA: how much power it can pass without overheating.
Commercial package: what a transformer quote may contain
B-006 Current transformer
B-007 Voltage transformer
B-008 Protection relay
B-018 Control / protection panel
B-033 Fan / pump bank
B-022 MV ring main unit (in EXCOOL quote)
B-009 Revenue meter (in EXCOOL quote)
B-017 Neutral earthing resistor
B-026 MV cable and terminations
B-034 Prefab eHouse: housed is not included
B-015
Main power transformer
parent line
Included only if vendor scope says so
Usually separate
HISTORICAL Q2 2021
EXCOOL cost plan, London, supply only: 2.5 MVA £75,000 and 3.0 MVA £90,000, both £30/kVA, quoted with RMU and metering unit. One plan gives two points on one line, with no market curve.
CURRENT PRICE GAP
No current public price for transformers of this class. Use a tender, award or OEM quote with scope.
Notes: A transformer is the simplest big machine in the building. Two coils of wire wrap around a shared iron core. Alternating current in one coil creates a changing magnetic field in the core, which induces a voltage in the other coil. The ratio of turns sets the ratio of voltages. More turns on the high-voltage side, fewer on the low-voltage side, and you step the voltage down. The tank holds an insulating liquid that also carries heat to external radiators, which is why there are fan or pump banks on large units. A transformer is sized in kVA or MVA, the apparent power it can pass without overheating. That is your quantity driver. Redundancy sits on top: how many transformers are needed so that losing one still leaves enough capacity. Now the commercial point. When you buy a transformer you rarely buy only the tank and coils. The ontology freezes a package control for the parent line B-015. The current transformer, voltage transformer, protection relay, control panel and fan bank are only suppressed as separate lines when the vendor scope says they are included. The amber colour means conditional, never assumed. On the right side, the reference cost plan quotes its transformers together with a ring main unit and a metering unit. So a model that takes that price and also adds a separate RMU and meter would double-count. A prefabricated eHouse or substation module is a different trap. The module houses equipment, and the ontology rule is blunt: housed is not included. The vendor bill of materials decides. On evidence, the only numbers we have are historical. The cost plan from the second quarter of 2021 prices a two-and-a-half MVA unit at seventy-five thousand pounds and a three MVA unit at ninety thousand pounds. Both work out at thirty pounds per kVA. This is supply only, in London, five years old, and from one document. Two points on one line tell you the cost plan scaled linearly. They add nothing about the wider market. Currentising it is an explicit modelling step, which we cover later. The current public price for this class is an open gap.

## Slide 8
ELECTRICAL CHAIN | STANDBY GENERATION
A generator set is five sub-systems that must all work on the day
Genset package, often with acoustic enclosure C-021 and container C-022
Engine subsystem
C-004
Lube oil C-026
Jacket water C-025
Coolant tank C-030
Crankcase vent C-027
Alternator
C-003
turns shaft rotation into electricity
Control panel
C-005
start, sync, protect
shaft
Bulk tank
C-009
Transfer pump C-010
Polish / filter C-011, C-012
Day tank C-008
FUEL
EXHAUST
SCR C-016 / DOC-DPF C-017
Silencer C-014
Stack C-015
Radiator / remote cooler C-018
COOLING
Starting battery C-019
Block heater C-020
Output breaker
C-007
Paralleling
switchgear C-006
to LV board and UPS input
Load bank C-023
(permanent test load)
First principles
Diesel burns, the engine turns a shaft, the alternator makes AC. It must start and take load in seconds, because the UPS battery only bridges minutes.
Quantity driver
Critical MW, generator block size and redundancy (QG). Autonomy in hours of fuel is a separate driver (QV): tank volume.
Why finance cares
Emissions permits, running-hour limits and fuel logistics can cap how much the backup is worth, whatever the nameplate says.
Notes: A standby generator is a power station in a box, and it is easiest to understand as five sub-systems that all have to work together on the day. Fuel on the left. Fuel sits in a bulk tank, is moved by a transfer pump, is filtered and polished so water and sediment do not clog the engine, and is held in a small day tank next to the engine. Autonomy, meaning how many hours the site can run without refuelling, is set by tank volume. That is a storage driver, separate from the generator rating. The engine in the middle burns fuel and turns a shaft. Around the engine are the support systems: lubrication, jacket-water cooling, a coolant header tank and crankcase ventilation. The alternator on the same shaft turns rotation into electricity. The local control panel starts the set, synchronises it with other sets and protects it. Exhaust is on top. Gas leaves through emissions treatment, where the SCR or particulate filter sits, then a silencer, then a stack. Cooling is at the bottom, with a radiator or remote cooler that rejects engine heat. A starting battery and a block heater keep the engine ready to start quickly. A permanent load bank lets operators test the set without touching the live load. On the right the electricity goes through the output breaker and the paralleling switchgear, which lets several sets share a bus, and then on to the LV board and the UPS input. Why does the UPS matter here? The generator needs seconds to start and stabilise. The UPS battery covers that gap. So the reliability of the whole site depends on the handshake between these two systems, which commissioning must prove. For finance, three things. First, the nameplate megawatt is only valuable if permits allow it to run and the fuel can be delivered. Second, most of the boxes on this diagram can appear as their own ontology line and as a child inside a complete-set price, which is the next slide. Third, generators have large service and overhaul needs. The ontology holds no numeric life for them, because engine families differ, and it warns against inferring overhaul hours across families.

## Slide 9
ELECTRICAL CHAIN | GENERATOR PACKAGE
A complete genset price already contains most of its own parts
C-003 Alternator
C-004 Engine subsystem
C-005 Local control panel
C-019 Starting battery / charger
C-025 Jacket-water pump
C-026 Lube-oil system
C-027 Crankcase ventilation
C-030 Coolant expansion tank
C-007 Output breaker
C-008 Day tank
C-014 Exhaust silencer
C-015 Exhaust stack
C-016 SCR emissions package
C-017 DOC / DPF emissions
C-018 Radiator / remote cooler
C-020 Jacket-water / block heater
C-021 Acoustic enclosure
C-001
Diesel / HVO generator set
complete package price
Usually included (frozen rule)
Included only if vendor scope says so
No frozen rule: confirm per quote
Outside the frozen rules, confirm per quote:
C-006 Paralleling switchgear
C-009 Bulk fuel tank
C-011 Fuel polishing skid
C-023 Permanent load bank
HISTORICAL Q2 2021
EXCOOL, supply only, with 24h belly tank and NER: 2,000 kW £637,500, 2,500 kW £765,000, 3,000 kW £941,250. That is £319, £306 and £314 per kW.
CALIBRATION ONLY
Marketplace 2 MW asks calibrate, never price. The Cardonald generator award (£187,377, rating absent) includes wiring and switchgear.
Notes: This slide is about double-counting, which is the most common way a bottom-up cost model overstates capex. In the middle is the parent line, C-001, the complete diesel or HVO generator set. When a vendor quotes a complete packaged genset, the quote normally includes the standard engine-generator assembly. The eight green chips on the left are the children the ontology freezes as default-included. If your model takes a complete-set price and also adds an alternator line, an engine line, a control panel line, a starting battery line and the rest, you are paying for the same machine twice. The ontology's rule is to suppress those children's acquisition capex and keep them in the model for lifecycle and replacement analysis. That distinction matters. The alternator can still wear out and appears in the replacement schedule, even without a separate purchase line. The amber chips on the right are conditional. The output breaker, day tank, silencer, stack, emissions packages, radiator, block heater and enclosure are included only when the vendor's scope says so. There is no universal assumption frozen, because vendors differ. A complete set with a sound-attenuated enclosure includes the enclosure. A bare set does not. A site with a remote radiator excludes the radiator from the set price. Your job is to read the quote. The white chips are outside the frozen rules. Paralleling gear, the bulk tank, polishing skids and the permanent load bank often sit in separate packages. No rule exists, so confirm each one. At the bottom, the evidence. The reference cost plan from the second quarter of 2021 gives three generator points with a twenty-four hour belly tank and neutral earthing resistor included, supply only. They are around three hundred and six to three hundred and nineteen pounds per kW. That is a historical package anchor. It dates from 2021. For current evidence the picture is weaker. Marketplace asking prices exist for two-megawatt sets. Asking prices, used units and unspecified configuration make them calibration only. The Cardonald award is an executed price, which is strong. It bundles a generator with wiring and switchgear and does not state the rating. It is installed-package evidence. It cannot be unit-normalised.

## Slide 10
ELECTRICAL CHAIN | UPS FIRST PRINCIPLES
A UPS converts power twice so the load never feels the grid
Utility AC
input
Input
switchboard
D-006
Rectifier
AC to DC
DC bus
Inverter
DC to AC
Output
switchboard
D-007
Critical AC
load
DC fuse / breaker
D-023 / D-014
Battery strings
VRLA D-010 or Li-ion D-011
racks D-012
Battery management D-013
monitoring D-015
Static bypass switch D-004
(fast electronic transfer)
Maintenance bypass switch D-005 (manual)
Why two conversions? The inverter output is rebuilt from DC, so grid noise, sags and short outages never reach the servers.
Quantity driver (QU): protected kW + minutes of runtime + redundancy
1 Normal
Load runs through rectifier and inverter. The battery floats on the DC bus.
2 Grid fails
Battery feeds the inverter with no break. Runtime clock starts while generators start.
3 Fault or overload
Static bypass moves the load to raw mains in a fraction of a cycle.
4 Maintenance
Manual bypass feeds the load so the UPS can be isolated and worked on.
Notes: The UPS, or uninterruptible power supply, answers a simple question. What keeps the servers running during the seconds between a grid failure and the generators taking over, and what cleans the power in the meantime? Follow the amber line. Utility AC comes in through an input switchboard to the rectifier. The rectifier turns AC into DC. That DC sits on a DC bus. The inverter turns the DC back into clean AC and sends it through an output switchboard to the critical load. Converting twice looks wasteful, and it costs a little efficiency. The payoff is an output rebuilt from scratch. Grid noise, sags and brief outages never reach the servers. The batteries hang off the DC bus below, through a fuse or breaker. In normal operation they float, charged and waiting. When the grid fails, they discharge into the DC bus and the inverter carries on without a break. A battery management system and monitoring watch the strings. The runtime is whatever the battery energy and the load allow. Think minutes, not hours, because the generator exists for the long haul. Now the two bypasses, which matter more than people expect. The teal line is the static bypass. It is an electronic switch. If the UPS has a fault or sees an overload, the static bypass moves the load directly to mains power in a fraction of a cycle. The violet dashed line is the maintenance bypass. It is a manual switch that lets engineers isolate the whole UPS for service while the load stays powered on raw mains. The four boxes at the bottom are the operating modes. Normal, grid fails, fault or overload, and maintenance. Ask any operator which mode the site spends time in and how often they exercise the others. The quantity driver, QU, is protected kilowatts plus minutes of runtime plus redundancy. A UPS rated in kVA and kW is sized to the load. Its battery is sized to the runtime. Those are two different cost drivers, and the next slide shows why they are often priced together and sometimes priced apart.

## Slide 11
ELECTRICAL CHAIN | UPS AND BATTERY PACKAGE
UPS evidence spans three scales and none is a current MW price
D-004 Static bypass switch
D-005 Maintenance bypass
D-010 VRLA battery string
D-011 Li-ion battery cabinet
D-012 Battery rack / cabinet
D-013 Battery management
D-014 Battery breaker + DC fuse
D-015 Battery monitoring
D-022 DC cable / interconnect
D-006 Input switchboard
D-007 Output switchboard
D-020 Isolation / input transformer
D-021 Output / step-down transformer
D-018 Battery-room ventilation
D-019 Battery fire-detection interface
D-024 Prefab UPS module: housed is not included
D-025 Capacitor / fan service kit
D-001 / D-002
UPS frame (monolithic or modular)
parent line
Included only if vendor scope says so
Usually separate
Lifecycle / replacement item
CURRENT, WRONG SCALE
APC 10 kVA / 10 kW rack UPS: $12,022 reseller, $18,355 list (observed 2026-10-05). The UPS plus transformer bundle is a different scope. Neither scales to MW.
HISTORICAL Q2 2021
EXCOOL: 1,660 kVA UPS with 15 min batteries £323,700, or £195/kVA, supply only, battery monitoring excluded. Output switchboard 3,000 A £105,000 priced separately.
EXECUTED PACKAGE
Southern Water UPS framework lot £4.8m, supply and install, quantities and ratings undisclosed. Package scale only, no unit rate.
CURRENT PRICE GAP
MW-class UPS with batteries has no current public price. Needs OEM quote, tender return or award with runtime, chemistry and scope.
Notes: On the left side of this hub are the children that may sit inside a UPS price. Static bypass, maintenance bypass, the battery strings or Li-ion cabinets, racks, the battery management system, the DC breaker and fuse, monitoring and the DC interconnect. The ontology freezes these as conditional. They are suppressed as separate acquisition lines only when the vendor scope says the UPS package includes them. It never assumes it. On the right are items usually priced separately. Input and output switchboards, isolation and step-down transformers, battery-room ventilation and the fire detection interface. One entry is a lifecycle item, the capacitor and fan service kit, which belongs in the replacement schedule and sits outside acquisition capex. And, again, a prefabricated UPS module houses equipment. It does not automatically include it. The batteries need special attention. The UPS frame is a power electronics asset. The battery is an energy store with a different chemistry, a different fire profile and a different replacement cycle. In a model, a combined price should be split back into those two lines for lifecycle, even if you used the package price for acquisition. The bottom row is the heart of the slide. It shows four kinds of price evidence on the same equipment family, and none of them lets you price a megawatt-scale UPS today. The first is current and observable. A small rack UPS has a posted price, both a list price and a reseller price, and the ontology keeps those apart and says do not average them. It is the right kind of evidence at the wrong scale. The second is a historical cost plan from 2021. It gives a package at real project scale, about one hundred and ninety-five pounds per kVA including fifteen minutes of batteries, supply only. It is a shape anchor. The third is an executed regional framework award. It tells you the order of magnitude of a procurement and nothing about unit rates. The fourth box says what it is. The current price for MW-class UPS and batteries remains an open gap. The finance lesson is to match the evidence to the scale, and say out loud when you cannot.

## Slide 12
ELECTRICAL CHAIN | LV AND RACK DISTRIBUTION
The last 30 metres decide how much power a rack can actually use
UPS output switchboard
D-007 | amps
LV board, PDU, RPP
E-001, E-009, E-010 | amps
Busway and tap-off
E-011, E-012 | amps per feed
Rack whip and rack PDU
E-017 to E-019 | kW per rack
Server power supplies
A and B inputs | kW
Row elevation, simplified
Busway A
Busway B
Each rack has two independent feeds: an A rack PDU and a B rack PDU. Amber and teal never share a busway.
Tap-off boxes E-012 (small white squares)
Rack PDUs E-018, E-019 (vertical strips)
Read the chain as a chain of ratings
Density is capped by the thinnest link: tap-off amps, whip size, rack PDU or the breaker feeding it. A bigger UPS upstream does not fix it.
Quantity drivers: amps, fault rating, circuits, metres of busway and cable, racks
HISTORICAL Q2 2021
EXCOOL, supply only: main LV switchgear 4,000 A £128,000 and 5,000 A £155,000 (about £31 to £32 per A). PDU 24-way 630 A £23,000, excluding lift, cranage and FAT/SAT/IST. Installation is separate.
CURRENT, COMPONENT
A commodity breaker posts at $8.07 (THQP120). Assemblies stay quote-based (GP-E).
Notes: The last thirty metres of the electrical chain are where capacity becomes usable. Look at the chain at the top. The UPS output switchboard feeds an LV board, PDU or remote power panel. That feeds a busway with tap-off boxes. A tap-off box is a plug-in unit that connects a rack to the busway. A short cable called a whip, or a rack PDU, delivers power to the servers' power supplies. The elevation drawing shows the topology. Two busways run above a row of racks, A in amber and B in teal. Each rack takes one feed from each, so that if one path fails, every server still has the other. This is the physical form of two-N distribution that we cover on the redundancy slide. The key learning is that this is a chain of ratings. Any link can be the thinnest. The tap-off box has an amp rating. The whip has a size. The rack PDU has a breaker. A site may have a huge UPS and a perfectly good board, and still be unable to serve a rack of high-density GPUs because the final links were specified for air-cooled servers. That is why density is a diligence question for the physical path as well as for the cooling. On quantity drivers, this layer scales with amps, fault rating, circuit count, metres of busway and cable, and rack count. That is why it is often the least well captured item in a top-down dollars-per-megawatt number. On evidence, the historical cost plan gives us supply-only prices for main LV switchgear, about thirty-one to thirty-two pounds per amp at four and five thousand amps, and a PDU at twenty-three thousand pounds for a six hundred and thirty amp, twenty-four-way unit. Those exclude lifting, cranage and factory and site testing, and installation is a separate trade. On the current side, individual commodity breakers have public prices, a few dollars each. Do not read across. The ontology notes that switchboards and busway assemblies remain quote-based. A cheap breaker inside an expensive assembly tells you nothing about the assembly.

## Slide 13
ELECTRICAL CHAIN | REDUNDANCY
Redundancy changes how many units you buy at each layer
N just enough
1
1
1
1
Shared bus
IT load: 4 MW
N+1 one spare module
1
1
1
1
1
Shared bus
IT load: 4 MW
2N two full paths
1
1
1
1
Path A
1
1
1
1
Path B
IT load, dual-fed
Modules bought (1 MW each, 4 MW load)
4
5
8
Survives one module failing
No
Yes
Yes
Survives loss of a whole path or bus
No
No
Yes
Maintain without exposing the load
No
Partly
Yes
Not a percentage uplift. Generators, UPS, distribution and cooling can each carry a different topology, so apply redundancy layer by layer. Illustration only: 4 MW load, 1 MW modules, one layer.
Notes: Redundancy is the most misused word in data centre finance, so let us make it concrete with a simple example. A four megawatt load, served by one-megawatt UPS modules. In an N design you buy exactly what you need. Four modules. If any one fails, you lose capacity, and the load is exposed. If any shared component such as the bus fails, the load is down. In an N+1 design you buy one extra module, five in total. You can lose one module and carry on. You can also take a module out for maintenance. The five modules also feed a shared bus. If the bus fails, the load fails. N+1 protects against component failure and does not protect against the failure of the thing everything shares. In a 2N design you build two entire paths, each able to carry the whole load on its own. Eight modules in this example, with separate buses, and a dual-fed load. You can lose a whole path and keep running. You can maintain one path while the other carries the load. It is the most expensive and the most resilient. In practice it is applied at specific layers with real choices at each. The table summarises it. Modules bought are four, five and eight. Notice the jump from five to eight. The step from N+1 to 2N carries a real cost that varies with the layer. It depends on which layer you apply it to. The finance consequence is that you should never apply a redundancy uplift as a single percentage to total capex. Generators, UPS, distribution boards, chillers and room cooling units can each have their own topology. The reference facility in the 2019 CIBSE and AECOM cost model is a four-and-a-half megawatt Tier III design, with room cooling units at N+2 and chillers at N+1. The cost plan from 2021 prices indirect air units at N+2 per hall. Those are layer choices, and you will see their effect in counts. When someone quotes a Tier rating, ask which layers carry which topology, and whether the quoted capacity is before or after the redundancy.

## Slide 14
THERMAL CHAIN | HEAT TO ATMOSPHERE
Heat has to be captured, carried and finally handed to the outside air
AIR PATH
IT heat
Server fans push hot air out of the rack
kW IT
Room capture
CRAH or fan-wall coil hands heat to water
G-001 to G-013
Water loop
Pumps move chilled water around the plant
F-013 to F-018
Chiller
Refrigerant cycle lifts heat to outdoor-ready level
F-001 to F-004
Heat rejection
Fans blow outside air over a coil or tower
F-005 to F-010
Atmosphere
Heat leaves the site
LIQUID PATH
Chip heat
Cold plates sit on the hottest chips
H-001
Rack capture
Manifolds and quick-disconnect hoses carry coolant
H-002 to H-005
CDU
Heat exchanger between rack loop and facility loop
H-006 to H-011
Facility water
Water or glycol loop to the plant
F-013 to F-016
Heat rejection
Dry or hybrid coolers, or a chiller if needed
F-007, F-008, F-010
Atmosphere
Heat leaves the site
First principle
Almost every kW of IT power ends as a kW of heat (kWth). Chillers and fans add a little more.
Design temperature is a choice
The EXCOOL plan sizes chillers for 21/31 °C water with 20% glycol. Warmer loops reject heat more easily.
Where the money sits
Branch F plant is shared by both paths. Branches G and H differ by how heat is captured.
Notes: The thermal chain is harder to see than the electrical chain, so we will draw it carefully. The job is simple. Take heat from where it is made, carry it somewhere, and give it to the outside air. Every step in the chain exists because heat only flows from hot to cold, and the outside air can be only so cold. The top row is the familiar air-cooled path. The IT equipment turns almost all the power it draws into heat. Server fans push hot air out of the rack. A room cooling unit, a CRAH or a fan-wall, has a coil carrying cold water. The hot air passes over the coil, gives up its heat and returns cool. The water now carries that heat through pumps and pipes, called the hydronic loop, to the chiller. A chiller is a refrigeration machine. It uses a compressor and refrigerant to lift the heat to a temperature at which the outside air can accept it. A heat rejection device, a condenser, dry cooler or cooling tower, finally blows outside air over a coil to carry the heat away. The bottom row is the liquid path. Here cold plates sit directly on the hottest chips. Coolant flows through manifolds and flexible hoses with quick-disconnect couplings. A coolant distribution unit, the CDU, keeps the rack loop separate from the facility loop and exchanges heat between them. The facility water then goes to heat rejection. Because liquid can run warmer, some designs reject heat with dry coolers alone for much of the year. Do not assume that, as it depends on the design and the climate. The labels at the bottom of each box are ontology branches. F is central plant, G is white-space air cooling, H is liquid cooling. The three cards on the bottom give the finance lens. First principle: kilowatts of IT become kilowatts thermal, so cooling is sized to heat. Second: design temperature is a choice with cost consequences. The reference cost plan sizes chillers for twenty-one to thirty-one degree water with twenty percent glycol. Third: central plant is shared, while capture differs. That is why a liquid-cooled hall and an air-cooled hall can share a plant and still have very different white-space capex.

## Slide 15
THERMAL CHAIN | CHILLERS AND HYDRONICS
A chiller is one box inside a plant, and each quote draws the box differently
Refrigeration cycle
Compressor
raises pressure and temperature
Condenser
rejects heat to outside air
Expansion valve
drops pressure, so it chills
Evaporator
absorbs heat from the water
to air
warm in
cool out
Four chiller types in the ontology: air-cooled screw F-001, air-cooled centrifugal or magnetic-bearing F-002, water-cooled screw F-003, water-cooled centrifugal F-004.
Hydronic plant: what moves the water
Primary pump + VFD
F-013, F-016
Strainer
F-029
To white space
CRAH, CDU
Buffer tank
F-018
Air / dirt separator
F-024
Return from white space
Expansion vessel
F-017
Glycol fill, treatment
F-027, F-021 to F-023
Plate HX / economiser
F-011, F-025
Chiller F-001 to F-004 plumbs into this loop.
Packaged pump room F-026 may bundle pumps, VFDs, vessels, separators, strainers and controls (package rules PKG-083 to PKG-091).
Q2 2021, UK
Air-cooled chiller 1,660 kWth: £498,750 = £300 per kWth, supply only, compressor type not stated.
≠
2019, UK notional
Air-cooled chillers N+1 with CHW pipework, pumps and associated plant: £890 per kW IT, 4.5 MW Tier III.
Notes: Start on the left with the refrigeration cycle, the beating heart of a chiller. A refrigerant gas circulates in a closed loop through four components. The evaporator is where cold refrigerant absorbs heat from the building's chilled water, which returns warm and leaves cool. The compressor raises the refrigerant's pressure and temperature, so it is hotter than the outside air. The condenser then rejects that heat to the outside air, using fans on an air-cooled chiller. The expansion valve drops the pressure, which chills the refrigerant again, and the cycle repeats. The ontology holds four chiller types, differing in compressor and in how they reject heat. On the right is the part people forget. A chiller does not work alone. Water has to be moved, cleaned, kept in volume and protected. A primary pump with a variable-frequency drive circulates it. Strainers and an air and dirt separator protect the system. A buffer tank smooths load. An expansion vessel absorbs volume changes as temperature moves. A glycol fill and treatment skid keep the fluid safe. Plate heat exchangers and an economiser can provide free cooling when the weather helps. All of this is hydronics. Commercially, this is a package puzzle. The ontology has a packaged pump room line, F-026. If a vendor sells a pump skid, the pumps, drives, vessels, separators, strainers and controls may all be inside. The package controls freeze that as conditional on the vendor bill of materials. Now the strip at the bottom is a lesson in scope. On the left, a chiller at three hundred pounds per kilowatt thermal, from the 2021 cost plan. On the right, a chiller line at eight hundred and ninety pounds per kilowatt of IT load, from the 2019 CIBSE and AECOM cost model. They look like two prices for one thing. They differ on four counts. The units differ, kilowatt thermal against kilowatt of IT. The scope differs, a supply-only chiller against chillers plus chilled-water pipework, pumps and associated plant. The year differs. The redundancy differs. The ontology flags the second as a multi-component package that includes more than the chiller. Never put them in the same column.

## Slide 16
THERMAL CHAIN | INSTALLED COOLING PACKAGES
Three cooling architectures, priced as installed packages, per kW of IT
Chart: GBP per kW IT, 2019
| Conventional (chillers + CRAC) | Indirect air cooling (IAC) | Hybrid (cooler + chillers)
Room cooling units (CRAC, N+2) | 240 | 0 | 0
Chillers + CHW pipework + pumps (N+1) | 890 | 0 | 0
IAC units (N+2) | 0 | 760 | 0
IAC process water, storage, pumps, duct | 0 | 220 | 0
Hybrid cooler + water-cooled chillers + networks | 0 | 0 | 1130
Room cooling, implied (not itemised) | 0 | 0 | 240
BMS controls + power supplies | 320 | 280 | 350
HISTORICAL 2019, UK notional
CIBSE/AECOM Table 2 | 4.5 MW IT | Tier III | not escalated
Totals: £1,450, £1,260, £1,720
Use the total or the components, never both. The ontology suppresses constituents when a total is active.
£1,130 appears twice in history
An earlier extract wrongly showed £1,130 as the conventional total. It is the hybrid mechanical line only. £1,450 supersedes it.
Controls are about a fifth
BMS controls and power supplies are £280 to £350 per kW, roughly 20% to 22% of each total.
Scale it to see the size
At 4.5 MW IT: about £6.5m conventional, £5.7m IAC, £7.7m hybrid, in 2019 money. Arithmetic on the reference facility only.
Notes: This chart shows the best installed-package cooling evidence in the ontology. The 2019 CIBSE and AECOM cost model prices three cooling options for a reference four-and-a-half megawatt, Tier III data centre. Each bar is a total installed cost per kilowatt of IT load, built from components. The conventional option is room cooling units at two hundred and forty pounds, air-cooled chillers with pipework, pumps and associated plant at eight hundred and ninety, and controls and power supplies at three hundred and twenty. That sums to fourteen hundred and fifty pounds per kW of IT. The indirect air cooling option is units at seven hundred and sixty, a process water and ductwork support package at two hundred and twenty, and controls at two hundred and eighty, for twelve hundred and sixty. The hybrid option is a hybrid cooler with water-cooled chillers and networks at eleven hundred and thirty and controls at three hundred and fifty, for seventeen hundred and twenty. A careful reader will notice that eleven hundred and thirty plus three hundred and fifty is fourteen hundred and eighty, not seventeen hundred and twenty. The difference is two hundred and forty. That matches the room cooling line in the conventional option, so the likely explanation is that room cooling is part of the hybrid total and was not extracted as a separate line. I have drawn it as the lighter violet block and labelled it as implied. That is my inference and no source figure. The total is the anchor. Three rules from the ontology. Use the total or the components, never both, because the package controls suppress one when the other is active. The eleven hundred and thirty figure belongs to the hybrid option and must not be used as the conventional total, which an earlier research pass did by mistake. And controls matter. At roughly a fifth of each total, they are a material line that is easy to omit. At the bottom right is a scaling illustration. Multiply the per-kW rates by forty-five hundred kilowatts and you get roughly six and a half, five and a half, and seven and three-quarter million pounds. That is the 2019 reference facility, in 2019 money. This answers 'what did one design cost to install in 2019?' and leaves 'what does cooling cost today?' open. Escalating it is a separate, explicit step. It is historical evidence.

## Slide 17
THERMAL CHAIN | WHITE-SPACE AIR COOLING
Three ways to cool a hall with air, each moving the heat differently
CRAH on a raised floor
G-001, G-010 to G-013
blue: cold air red: hot air
CRAH
hot air returns overhead
Fan-wall array
G-004, G-006
blue: cold air red: hot air
coil
Indirect air cooling (IAC / AHU)
G-005
blue: cold air red: hot air
IAC unit
air-to-air exchanger
outside air cools the hall air through the exchanger
Heat leaves via chilled water to chillers
Sized by kW sensible and N+x units
Heat leaves via chilled water to chillers
Sized by kW sensible, airflow and N+x
Heat leaves to outside air, trimmed by chillers
Sized by kW sensible, N+2 per hall
HISTORICAL Q2 2021
EXCOOL, supply only: DX CRAC 50 kW £33,000 (£660/kW, plantroom unit, not a white-space CRAH). IAC 250 kW sensible: direct £88,000 (£352/kW), indirect £66,000 (£264/kW). 357 kW IAC at £92,400 includes controls, spares and training, so it is not like-for-like.
CURRENT PRICE GAP
CRAH and fan-wall project pricing is scarce in public sources (gap profile GP-G).
Notes: Three different ways to cool a hall with air. The common job is the same. Keep the cold aisle cold, remove the hot aisle's heat, and avoid mixing the two. On the left is the classic design. A computer room air handler, a CRAH, stands at the edge of the hall. It blows cold air into the void under a raised floor. Perforated tiles let it rise into the cold aisle in front of the racks. Servers pull it through, and the heated air rises at the back, returns overhead and goes back to the CRAH coil, which is cooled by chilled water from the central plant. Containment panels in the ontology stop hot and cold air mixing. In the middle is a fan wall. A wall of electronically commutated fans sits in front of a cooling coil and pushes cooled air across the hall, in place of a few big air handlers. Many small fans give resilience and fine control. The heat still leaves by chilled water. On the right is indirect air cooling. The hall air stays in a closed loop. It passes through a large air-to-air exchanger, and outside air passes the other side, never mixing. When the weather is cool enough, outside air does all the work. The ontology notes that chillers may only trim, and the cost plan describes a trim chiller used about one percent of the year in one hybrid design. The quantity driver for all three is kilowatts of sensible cooling and the redundancy count, N+1 or N+2. Sensible means the ordinary temperature-changing heat, as opposed to humidity-related latent heat. On pricing, the evidence is historical and uneven. The 2021 cost plan has a DX CRAC at six hundred and sixty pounds per kW, and note that it is a plantroom unit, a different item from a white-space CRAH. Indirect air cooling units come in cheaper per kW than direct air in that plan. One line, the three-hundred-and-fifty-seven kW unit, includes controls, spares and training, and the ontology says you cannot compare it with the others on kW alone. Public current pricing for CRAHs and fan walls is scarce. Treat everything here as shape.

## Slide 18
THERMAL CHAIN | DIRECT-TO-CHIP LIQUID COOLING
Direct-to-chip cooling brings the coolant to the chip itself
Rack
To CDU
Cool room air still serves memory, drives and power supplies
Cold plates H-001 sit on the hottest chips
Quick-disconnects H-005 (amber dots) allow servers to be pulled without draining
Rack manifolds H-002: supply blue, return red
Hoses H-004 and supports H-033, row manifold H-003, leak detection H-014
Simplified. Real servers carry many plates and parallel micro-channels.
First principles
Water holds more than 3,000 times more heat per unit volume than air. Moving coolant to the chip removes heat at the source, so far fewer fans are needed in the room.
Quantity driver
Cold plates, manifolds and quick-disconnects scale per rack (QR). CDUs scale with thermal load (QC). Coolant is a volume in litres (QF).
Commercial risk
Liquid-ready and liquid-installed are different states. Warranty, hose and coupling quality and leak response sit with several parties.
CURRENT PRICE GAP
Liquid cooling is largely quote-based. Public price is very weak and tenders are emerging (GP-H), so no number is shown.
Notes: Direct-to-chip cooling is the technology behind high-density AI racks. The idea is simple. Put the coolant on the chip. In an air-cooled server, fans push air over heat sinks and the heat ends up in the room. In direct-to-chip, a metal cold plate sits on the hottest chips, the CPUs and GPUs. Coolant flows through it and carries heat away through tubes. On the diagram the small teal squares are cold plates. Blue tubes bring cool coolant to them and red tubes take warm coolant away. Vertical manifolds on each side of the rack distribute and collect it. Quick-disconnect couplings, the amber dots, let operators pull a server out without draining the system. A row manifold at the bottom gathers the flow from several racks and sends it to the CDU, which we look at next. Why bother? From first principles, water holds more than three thousand times more heat per unit volume than air. That is why a thin pipe can carry what takes a roar of fans in air. It lets rack densities rise beyond what air can handle. The orange arrow on the left is a reminder that cold plates take the hottest chips. Memory, drives and power supplies still shed heat into the air, so you still need some air cooling. Hybrid is the normal case. For quantity drivers, three things scale differently. Cold plates, manifolds and quick-disconnects scale per rack. CDUs scale with thermal load. Coolant scales with litres, the volume in the loop. Commercial risk is the distinction between liquid-ready and liquid-installed. A hall can have the space, the pipe routes and the plant capacity, and still have no cold plates in any rack. Responsibility is shared. The server maker owns the plates, the rack integrator the manifolds, the facility the CDUs and pipework, and the customer the hardware warranty. When a leak happens, who pays is a contractual question that diligence should answer in advance. On evidence, the red badge applies. Public prices for liquid cooling are very weak and tenders are only emerging. The ontology flags the plates, the manifolds and the CDU family as provenance evidence of what exists and no price evidence. So no number is shown on this slide, deliberately.

## Slide 19
THERMAL CHAIN | COOLANT DISTRIBUTION UNIT
A CDU is a heat exchanger with pumps, filters and a brain
CDU
Plate heat
exchanger
H-010
Pump module
duty + standby H-009
Filtration
H-011
Expansion / buffer
tank H-030, H-031
Control valve
(facility side)
Controller / PLC H-015
Coolant-quality sensors H-012
Leak detection H-014
Air separator H-032
Fill / make-up H-029
Technology loop (TCS)
clean, controlled coolant to and from the rack manifolds
cool supply to racks
warm return from racks
Facility water loop (FWS)
plant water that carries the heat away
cool supply from plant
warmed return to plant
The two loops never mix. Heat crosses the plate wall.
Physical job
Isolate the delicate chip loop from building water, hold coolant temperature and flow, and filter the fluid.
Quantity driver
Thermal load (kWth) or rack count, depending on form factor: in-rack H-006, in-row H-007, facility-scale H-008. Pumps and CDUs add N+1.
Commercial risk
'CDU' can mean a rack box or a plant-room skid. The quote may or may not include pumps, heat exchanger, filters and controls.
Notes: This is the slide that turns a black box into a system. A coolant distribution unit, the CDU, sits between the delicate rack loop and the facility's water. Start with the two loops. On the left in amber and blue is the technology loop, sometimes called the secondary or TCS loop. It carries clean, controlled coolant to the racks and returns it warm. On the right in teal is the facility water loop, which carries the heat to the plant. The two loops never mix. Heat crosses the thin metal plates of the plate heat exchanger in the middle. Why separate them? Because the chips need a very clean, chemically controlled fluid at a stable temperature. Building water is dirtier and shared. The CDU is the gatekeeper. Now the components inside, which are all ontology lines. A pump module with duty and standby pumps keeps the coolant moving. A filtration module catches particles. An expansion or buffer tank absorbs volume changes. An air separator and fill and make-up keep the loop topped up and free of bubbles. A control valve on the facility side modulates how much facility water flows, which controls the coolant temperature. A controller or PLC runs all of it. Coolant-quality sensors and leak detection watch for trouble and can trigger alarms or shutdown. Why does a banker need this? Because 'CDU' names a product family and defines no scope. It might mean a small box in a rack, a unit between two racks or a plant-room skid serving a whole hall. A quote for a CDU may include the pumps, the heat exchanger, the filters and the controls, or some of them. If you price pumps and controls separately and the quote already contains them, you pay twice. If the quote excludes them and you assume it includes them, you under-budget. Quantity drivers follow thermal load. A CDU is rated in kilowatts thermal. How many you need is thermal load divided by unit capacity, plus redundancy. The manufacturers we see disclose redundant pumps, filtration and controls as part of the architecture, which tells us what is inside. It does not tell us the price.

## Slide 20
THERMAL CHAIN | CDU COMMERCIAL PACKAGE
No CDU scope is frozen, so every quote needs a bill of materials
Three form factors, three scales
In-rack CDU
H-006 | per rack (QR)
In-row CDU
H-007 | per block (QC)
Facility CDU
H-008 | per block (QC)
Bar length is symbolic, not to scale.
H-009 Pump module
H-010 Plate heat exchanger
H-011 Filtration module
H-015 Controller / PLC
H-012 Coolant-quality sensors
H-014 Leak detection
H-003 Row / facility manifold
H-004 Flexible hoses
H-005 Quick-disconnects
H-013 Coolant fill (litres)
H-030 Expansion / buffer tanks
H-032 Air separator
H-006 to H-008
CDU quote
scope per vendor
No frozen rule: confirm per quote
Usually separate
Diligence questions for any CDU quote
1 Which of pumps, exchanger, filters, controls and sensors are in the price?
2 Is redundancy inside the unit, or created by buying N+1 units?
3 Who supplies the coolant and the first fill?
4 Who owns warranty if a hose, coupling or fluid fails?
CURRENT PRICE GAP
CDU public price is very weak. OEM disclosures of redundant pumps, filtration and controls describe architecture, with no price.
Notes: Compare this slide with the generator and UPS package slides. There, the ontology froze rules about which children sit inside the parent price. For CDUs it has not. That is why every chip on the hub is white or grey. No inclusion rule exists, so no assumption is safe. The left side shows three forms of CDU. An in-rack CDU serves one rack and scales per rack. An in-row CDU serves a row or a block of racks. A facility-scale CDU serves a larger thermal block, typically in a plant room. The ontology classifies the first as a per-rack driver and the other two as per thermal block. The bars are symbolic. They show only that these are different scales. On the hub, the left chips are items that may sit inside a CDU quote. Pump module, plate heat exchanger, filtration, controller, coolant-quality sensors, leak detection, expansion tanks and the air separator. The right chips are items usually outside, such as the row manifold, hoses and quick-disconnects, and the first coolant fill, which is a volume driver. Those are tendencies and no rules. The only way to settle the boundary is to read the vendor's bill of materials. Four diligence questions are listed. Which of the internal parts are in the price? Is redundancy inside the unit, for example duty and standby pumps, or created by buying extra units? Who supplies the coolant and the first fill? Who owns the warranty if a hose, a coupling or the fluid fails? Notice that all four are about boundaries and responsibilities. None is about price. On evidence, the current public price for CDUs is very weak, and the ontology records it as a gap. Where manufacturers publish architecture, such as redundant pumps and filtration, that evidence helps you build a checklist. It does not give you a unit rate. A quote or a tender return, with scope stated, is what you need. Until then, carry a clearly labelled placeholder range or exclude the item from the point estimate and flag it.

## Slide 21
THERMAL CHAIN | REAR-DOOR AND IMMERSION COOLING
Rear doors extend air halls, and immersion replaces air altogether
Rear-door heat exchanger | H-016 to H-019
room air in
room-neutral air out
Fan module
H-018 (active only)
Valve / control
H-019
water to and from the facility loop
Heat is caught as it leaves the rack. The hall stays an air hall.
Immersion cooling | H-020 to H-027
dielectric fluid H-021 / H-022
Pump H-023
filter H-024
Heat exchanger /
CDU H-025
facility water
Service kit: hoist H-027, fluid cart H-026, drip tray H-035, fluid storage H-034.
Rear-door: what to ask
Passive or active? Active doors add fans and power. Door-water temperature, valve control and who owns leak response at the rack.
Immersion: what to ask
Single- or two-phase fluid? Fluid is a volume (QF) and a long-term asset. Floor loading, OEM warranty acceptance and hardware compatibility decide viability.
Evidence and lifecycle
No public numeric price. Fluid checks are scheduled, and the ontology holds no numeric fluid life, so none is shown. Do not infer one.
Notes: Two more liquid approaches, at opposite ends of the commitment spectrum. On the left, the rear-door heat exchanger. This is a radiator mounted on the back door of a normal rack. Servers still push hot air out the back. That air then passes through a water-cooled coil before it re-enters the room. The result is that heat is caught as it leaves the rack, and the hall can stay an air-cooled hall. A passive door has no fans and relies on the servers' own airflow. An active door adds fans, controlled by a valve and control unit. Because the rack stays a normal rack, rear doors are a common way to extend an existing air hall to higher density without rebuilding it. Water comes from the facility loop, which means water now runs to the back of each rack. On the right, immersion cooling. Servers sit in a tank of dielectric fluid, a liquid that does not conduct electricity. The fluid carries the heat away from every component at once. A pump circulates the fluid through a filter and a heat exchanger or CDU, which hands the heat to facility water. Single-phase fluid stays liquid. Two-phase fluid boils and condenses. The service tools are part of the system, a hoist to lift servers out, a fluid cart, drip trays and storage for fluid. For finance the questions differ. For rear doors, ask whether the doors are passive or active, what the door water temperature is, and who is responsible for leaks near live equipment. For immersion, ask what fluid is used and in what volume, because fluid is a quantity driver in litres and a long-lived asset. Ask about floor loading, since tanks are heavy. And ask about hardware compatibility and warranty. Not every server vendor will warrant immersed hardware, and a customer base that cannot use the tank limits its value. On evidence and lifecycle, the ontology says no public numeric price is available and, for fluid, it holds only qualitative service evidence. It specifically warns against turning a statement about scheduled fluid checks into an unsupported fluid life. So this slide has no numbers. That is the correct amount of numbers.

## Slide 22
THERMAL CHAIN | HYBRID COOLING LOGIC
Most real halls mix technologies, so liquid-ready needs three tests
Can air cooling serve the planned rack density?
Yes
Air hall
CRAH, fan wall or IAC (branch G)
No
Is this an existing air-cooled hall?
Yes
Add rear doors
RDHx extends the air hall (H-016, H-017)
No
Will the customer's hardware vendors accept immersion?
Yes
Immersion
Tank, fluid, pumps, CDU (H-020 to H-027)
No
Direct-to-chip plus residual air
Cold plates, manifolds, CDUs, plus air for the rest (H-001 to H-015, H-028)
Logic is a teaching simplification. Real choices also weigh climate, power, customer mix and cost.
Liquid-ready is a ladder, and each rung is separate capex
Rung 3 Liquid installed
Cold plates, rack manifolds, CDUs and fluid in service and commissioned
Rung 2 Plant and pipework ready
Headers, risers, plant capacity and CDU space provided and tested
Rung 1 Space and structure ready
Floor loading, riser routes and plant space reserved
HISTORICAL Q2 2021
EXCOOL 20 MW plan: the CHW installation line is £320,000 in the direct-air case and £5,688,000 where chillers serve the hall. Architecture moves installation cost as well as plant.
Notes: Almost no modern hall is pure. A hall serving AI training racks usually has liquid where the density is high and air for everything else. Three tests help you read what a seller says. Follow the decision tree on the left. First, can air cooling serve the planned density? If yes, build or keep an air hall. CRAHs, fan walls or indirect air units do the job. If no, the next question is whether this is an existing air-cooled hall. If yes, rear-door heat exchangers are the usual way to extend it, because they keep the rack and the room largely as they were. If no, ask whether the customers' hardware vendors accept immersion. If yes, immersion is an option. If no, the default for a new purpose-built high-density hall is direct-to-chip cooling with CDUs, plus air for the components that still need it. The ontology has a hybrid air-liquid rack enclosure line for that case. This tree is a teaching simplification. Real decisions weigh climate, power availability, customer mix and cost. Use it to ask 'which branch is this site on, and is that consistent with what the seller claims?'. On the right is the part that matters most for valuation. Liquid-ready is a ladder with three rungs. Rung one is space and structure. Floor loading, riser routes and plant space are reserved. Rung two is plant and pipework. Headers, risers and plant capacity are installed and tested, and space for CDUs exists. Rung three is liquid installed. Cold plates, manifolds, CDUs and fluid are in service and commissioned. Each rung is separate capex, and each is a separate claim. A seller who says the site is liquid-ready might mean rung one. The evidence strip shows why architecture matters. In the 2021 cost plan for a twenty megawatt hall, the chilled-water installation line is three hundred and twenty thousand pounds in the direct-air case, and five point seven million pounds where chillers serve the hall. The choice of technology moves installation cost as well as plant equipment. It is a London, 2021 cost-plan number, so use it for shape.

## Slide 23
ASSURANCE CHAIN | FIRE AND LIFE SAFETY
Fire protection is zoned by what burns and what water would destroy
Data halls
Early smoke detection (VESDA I-005), clean agent or pre-action sprinklers (I-009)
Electrical rooms
Switchgear, UPS: detection plus clean agent (I-013, I-014)
Battery room
Detection, ventilation (D-018) and suppression interface (D-019)
Meet-me room
Carrier and fibre: detection and agent
Control room
Fire panel I-001, firefighter interface I-026
Generator and fuel
Fuel area: detection, extinguishers, bunding
Outside the building: fire-water tank I-019, fire pump I-017, jockey pump I-018, hydrants I-025
Schematic plan. Real layouts vary by jurisdiction and insurer.
From detection to action
1
Detect
Smoke I-003, heat I-004, aspirating I-005
2
Alarm
Fire alarm control panel I-001, annunciators I-002
3
Release
Releasing panel I-012, cylinders I-013, nozzles I-014
4
Interface
Dampers I-022, I-028, smoke extract I-027, HVAC shutdown
5
Prove
Discharge, alarm and interface tests, with the authority
HISTORICAL Q2 2021
EXCOOL 20 MW, direct case: gaseous and fire suppression £1.72m; fire detection, alarm and VESDA £0.38m. Installed scope dominates cost.
Notes: Fire and life safety is an assurance system that lets the building be insured, permitted and operated. The plan view shows why a data centre has several different fire strategies. Fire protection is zoned by two questions: what could burn here, and what would suppression damage here? Water in a switchgear room is itself a hazard. Data halls typically use very early smoke detection, an aspirating system sometimes called VESDA, which pulls air through sampling pipes to a sensitive detector. Suppression is either a clean agent gas or a pre-action sprinkler, which keeps pipes dry until detection confirms a fire. Electrical rooms use detection plus clean agent. The battery room is its own problem. It needs ventilation for gases from lead-acid batteries, and, for lithium-ion, a suppression and detection interface. The ontology lists both ventilation and fire-detection interface as separate lines under the UPS branch. The generator area is about fuel. The control room hosts the fire alarm panel and the firefighter interface. Outside the building sit the fire-water tank and pumps. On the right is the chain of events. Detectors sense smoke or heat. The alarm panel decides. The releasing panel triggers agent cylinders or opens a valve. Interfaces shut dampers, start smoke extract and stop HVAC so the agent stays in the room. Then, importantly, someone proves it, through discharge and interface tests witnessed by the authority. For finance, three points. First, fire systems are mostly installed scope. Small devices have public prices. The system is the installation, and it is priced as a package. In the 2021 cost plan for a twenty-megawatt hall, gaseous and fire suppression installation is one point seven two million pounds and detection and alarm another three hundred and eighty thousand. Those are installed trade lines. Second, lifecycle intervals are driven by code, which varies by jurisdiction, and the ontology marks lifecycle evidence for fire as a gap. Third, acceptance matters. A site without a clean sign-off from the fire authority and the insurer is not bankable, regardless of how good the hardware is.

## Slide 24
ASSURANCE CHAIN | CONTROLS AND MONITORING
Controls hardware is cheap and public, and the integrated system is neither
Five layers, data up and commands down
DCIM
capacity, assets, customer reporting | K-020, K-021
BMS and EPMS
mechanical and power supervision | K-001, K-007, K-008, K-009 to K-012
Network and gateways
protocol bridges, monitoring Ethernet | K-006, K-022, K-027
Controllers
PLC, DDC, remote I/O | K-002, K-003, K-004
Field devices
sensors K-013 to K-019, actuators K-024 to K-026, meters
data
commands
Visible price versus installed system
tip
CURRENT
Catalogue hardware: PLC CPU $302, 15-slot base $228 (AutomationDirect)
Below the waterline
Integration, programming, head ends and wiring
£2.765m, same in all five EXCOOL cases (Q2 2021, 20 MW).
BMS controls and power supplies to mechanical plant
£320 per kW IT, about £1.44m at 4.5 MW (CIBSE/AECOM 2019).
Software licences and DCIM
Package prices weak (gap profile GP-K).
Notes: Controls and monitoring are the nervous system of the data centre. They are easy to dismiss as a small line, and for hardware they are. Let us separate layers. At the bottom are field devices. Temperature, humidity, pressure and flow sensors. Fuel-level sensors. Actuators that move valves and dampers. Meters. Above them are controllers. A programmable logic controller, or PLC, runs a control loop, such as keeping a chilled-water temperature. Remote I/O modules and direct digital controllers extend that reach. Above them is a network layer of gateways and protocol converters, which let equipment from different manufacturers talk. Above that sit the supervisory systems. A building management system, the BMS, supervises mechanical plant. An electrical power monitoring system, the EPMS, supervises power through meters and monitors. At the top is DCIM, data centre infrastructure management, which tracks capacity, assets and customer reporting. Data flows up. Commands flow down. Now the finance point, illustrated by the iceberg. Above the waterline is what you can see in a public catalogue. A PLC CPU costs a few hundred dollars. A base rack costs a hundred or two hundred. These are strong, structured, current observations. The ontology rates controls as one of the strongest public price categories. Below the waterline is the system. The 2021 cost plan carries two point seven six five million pounds for controls, head ends and control-system wiring on a twenty megawatt hall, and that number is the same in every cooling scenario. The 2019 CIBSE and AECOM model carries three hundred and twenty pounds per kW of IT for BMS controls and power supplies to mechanical plant, which is about one point four four million pounds at four-and-a-half megawatts. Those are installed, integrated packages. Software and DCIM package prices are weak in public sources. The lesson is about scale mismatch. Do not price a controls system by multiplying a catalogue PLC price by a point count. The cost is in design, programming, integration, testing and commissioning. And controls obsolescence is different from physical wear. The ontology says to model it separately. Ask who owns the licences and the configuration, because a buyer who cannot change the controls without the vendor is exposed.

## Slide 25
ASSURANCE CHAIN | FIBRE AND WHITE SPACE
Connectivity and rack space are what the customer actually buys
Diverse entrances
Two routes, two entry points | L-015
Meet-me room
Carrier racks L-001, frames L-002
Cross-connect
Frames and demarcation L-014, L-013
Trunks and raceway
Trunk L-009, raceway L-011
At the rack
Panels L-004, cassettes L-005, L-017, cords L-007
What a colocation customer rents, from small to large
Rack
M-001, M-002
per rack (QR)
Cage
M-008, M-009
per cage
Suite
private room
per suite
Hall
dedicated hall
per hall, kW
Every step adds committed kW, power, cooling and connectivity. Billing is usually kW or MW.
Landlord or tenant?
The EXCOOL plan excludes IT racks, hot/cold aisle containment, data cabling and servers from the build. Fit-out responsibility changes what capex a buyer inherits.
Why connectivity is value
Carrier density and diverse routes drive cross-connect revenue and customer stickiness. They are hard to replicate.
CURRENT
Passive fibre parts have strong public prices, e.g. a 24-fibre LC adapter panel at CNY 199 (native currency kept). Installed pathways are the real cost.
Notes: This slide is about what the customer actually buys. A data centre sells more than power and cooling. A colocation customer rents space and connectivity. Along the top is the physical path of a fibre. Carriers enter the building through diverse entrances, two routes at two entry points, so one dug-up duct does not isolate the site. They land in the meet-me room, where carriers and customers interconnect, using carrier racks and optical distribution frames. Cross-connect frames and demarcation cabinets mark the boundary of responsibility. Fibre trunks run through overhead raceways into the white space, and at the rack, patch panels, cassettes and patch cords terminate the cable. The steps below show the product ladder. A customer might rent a single rack, a locked cage, a private suite or a whole hall. Each step commits more kilowatts, and billing is usually in kilowatts or megawatts. For a lender the commercial unit is committed and drawn power with cooling and connectivity attached. Two commercial points. First, scope. The 2021 cost plan explicitly excludes IT racks, containment, data cabling and servers from the build. In a colocation model the landlord often provides shell, power, cooling and base connectivity, and the tenant provides racks and servers. Be clear which fit-out capex a buyer inherits. Second, connectivity is hard to replicate. A carrier-dense building with diverse routes earns cross-connect revenue and attracts customers who value latency and choice. That is value that sits outside the pure replacement-cost analysis, and it is a reason buy can beat build. On evidence, passive fibre components have strong, current public prices. The ontology preserves a Chinese catalogue price for a twenty-four fibre adapter panel in its native currency, not converted. As with controls, a component price is a tiny part of an installed pathway. Do not build a connectivity cost from catalogue parts.

## Slide 26
ASSURANCE CHAIN | WHICH MEGAWATT
The same site can have eight different megawatt numbers
1
Utility connection
contracted MVA or MW
utility
2
Energised
live and protection-approved
utility and engineer
3
Facility load
IT MW x PUE, includes cooling and losses
design engineer
4
Designed critical IT
kW delivered at the racks
design engineer
5
Redundancy-adjusted
N-available after N+1 or 2N
design engineer
6
Commissioned
integrated test passed under load
commissioning agent
7
Contracted
signed customer commitments
legal and sales
8
Billing
kW actually drawn or billed
metering and finance
Schematic, not to scale. The grey line under each bar names who confirms it. Always ask which step a quoted megawatt refers to.
Worked example. 20 MW of IT at a PUE of 1.3 draws 26 MW from the grid. Cooling and losses take the other 6 MW. Illustrative arithmetic only.
Notes: This is the slide that stops megawatts being used loosely. A single site can honestly be described with eight different megawatt numbers, and they are all real. Step one is the utility connection, the contracted capacity. Step two is energised capacity, live and approved. Step three is the facility's electrical load. This includes cooling, losses and everything else. It equals the IT load multiplied by the power usage effectiveness, or PUE. Step four is the designed critical IT capacity, the kilowatts delivered at the rack. Step five is redundancy-adjusted capacity, the N-available amount after reserve modules and paths are taken out. A hall with sixty megawatts of installed UPS modules in 2N might carry only about thirty megawatts of usable load. Step six is commissioned capacity, where an integrated test has passed under load. Step seven is contracted capacity, what customers have signed for. Step eight is billing capacity, what is actually drawn or billed. The colours group the steps. Amber is mostly electrical supply. Teal is design and test. Violet is commercial. The bars fall to the right to show that capacity is removed or proved at each step. The scale is schematic. Real values do not fall in a perfectly smooth sequence. The worked example is simple arithmetic. If twenty megawatts of IT run at a PUE of one point three, the facility draws twenty-six megawatts. The extra six megawatts goes to cooling and losses. That is why a grid connection quoted in megawatts and a revenue capacity quoted in megawatts are not the same thing, and the gap between them is a design variable. For diligence, make it a habit. When a seller or a model uses megawatts, ask which of the eight. When you compare capex per megawatt across assets, check that the denominators match. A cost per grid megawatt and a cost per billing megawatt can differ by a large factor in the same building. Most disagreements about cost per megawatt are really disagreements about which megawatt.

## Slide 27
ASSURANCE CHAIN | COMMISSIONING
Commissioning is the proof that converts installed equipment into capacity
Relative sequence, not to scale
Level 1 Factory witness tests (FAT)
Level 2 Delivery and installation checks
Level 3 Start-up and energisation
Level 4 Functional tests per system, with load banks
Level 5 Integrated systems test (IST) under full heat load
Handover Training, O&M documents, critical spares
Load banks O-001 and O-002 stand in for the IT load. Heat-load tests prove the cooling.
Which commercial state is the capacity in?
Included
in the price
Housed
inside a module
Installed
fixed and connected
Commissioned
tested under load
Accepted
customer and lender sign-off
0.4%
of the £100.5m EXCOOL direct-air cost is the itemised Level 1 to 5 test lines (£300,000 mechanical, £126,336 electrical), and it gates the revenue of all of it. Historical, Q2 2021.
Notes: Commissioning is the single most important concept in this assurance section, because it converts installed equipment into capacity a customer can use and a lender can rely on. The bars show the usual levels. Level one is factory witness testing. Engineers watch the manufacturer test the equipment before it ships. Level two is delivery and installation checks, confirming it arrived undamaged and was installed to specification. Level three is start-up and energisation. Level four is functional performance testing, system by system. Generators, UPS, chillers and CDUs are each run through their modes, often with load banks, which are devices that consume power and generate heat to simulate the IT load. Level five is the integrated systems test, the IST. Everything runs together under full heat load, and engineers inject failures to prove the redundancy works. They pull a utility feed, trip a generator, fail a chiller. Then comes handover, with training, operation and maintenance documents and critical spares. Below the Gantt are the five commercial states. Included, housed, installed, commissioned, accepted. Think of them as a ladder. A megawatt is only bankable at the commissioned and accepted rungs. A seller who says the capacity is installed may not have run the integrated test. A model that books capex when equipment is included in a price, or housed in a module, and revenue when it is installed, is mixing rungs. The red box makes a quiet point from the historical cost plan. The itemised Level one to five testing lines, mechanical and electrical, total about four hundred and twenty-six thousand pounds in the direct-air case. That is roughly point four percent of the one hundred point five million pound scenario cost. It is a tiny cost line that gates the revenue of the whole facility. Treat commissioning as a risk item. The ontology also carries load banks and critical spares, branch O, as maintenance and commissioning assets. For diligence, ask for the integrated systems test report, the open-defects list, whether seasonal tests were done, and whether the test covered the final configuration or an earlier phase.

## Slide 28
EVIDENCE | HOW EQUIPMENT IS BOUGHT
Every price source is born at a different stage of procurement
Design basis and specification
RFQ to OEMs, budget quote
Tender return, QS cost plan
Slot reservation and deposit
Award or purchase order
Factory test and delivery
Install, test, commission
Final account
CA3
OEM or distributor price
CA2
Tender return or QS cost plan
CA1
Executed award or contract
CA1
Final account, audited actual
Lead time bites here: slot, factory, shipping
Why award is not outturn: one real chiller project
Original award £3.55m
Later value, same project £4.52m (+27%)
Guildhall chiller replacement. Count it once.
Read the stage, then the price
A quote is an intention. A tender is a proposal. An award is a commitment. A final account is what happened. They answer different questions, and each can still be a broad package.
The ontology notes a later change notice on the same project must not be treated as a second observation.
Notes: To judge a price you need to know where in the buying process it came from. Equipment is bought in stages, and every stage creates a different kind of evidence. Start on the left. A design basis and specification define what is needed. The buyer sends a request for quotation to manufacturers and gets budget quotes. Those are OEM prices. In the ontology's evidence taxonomy this is commercial authority level three, usually equipment only and not installed. Next, a tender return or a quantity surveyor's cost plan gives a project cost. That is level two, strong project evidence that may differ from an executed price. Then there is often a slot reservation and a deposit, because manufacturing capacity for transformers, generators and large UPS is scarce. This is where lead time bites. After that comes the award or purchase order. An executed award is level one, the strongest commercial evidence, and it may still be a broad package. Then factory test, delivery, installation, commissioning, and finally the final account, the audited actual cost, also level one. The two bars show why you must not mix stages. A real chiller replacement project was awarded at about three point five five million pounds. The same project later carried a value of about four point five two million, an increase of twenty-seven percent. Both numbers are real. The first was the commitment, the second was closer to what happened. The ontology warns that a change notice on the same project is not an independent observation, so do not count both as two data points. For diligence, you should always ask three things about any price. Which stage produced it? Which scope does it cover? And has the number moved since? If a seller shows you a budget quote, you are looking at a stage-two number. If they show you a final account, you are looking at stage eight. And be aware of the lead-time zone. A buyer or a developer planning a new build is exposed between award and delivery, and a buyer of an operating asset is protected from it, which is part of the buy-versus-build argument later.

## Slide 29
EVIDENCE | HIERARCHY AND ADMISSIBILITY
Five grades of commercial evidence, and each one has a job
CA1
Executed award, contract, paid schedule or audited actual
Strongest. Still may be a broad package.
Cardonald generator award £187,377 (with wiring and switchgear). Southern Water UPS lot £4.8m. Guildhall chiller award.
CA2
Tender return, procurement schedule or formal QS cost plan
Strong project cost. Not an executed price.
EXCOOL cost plan (Q2 2021). CIBSE/AECOM cost model (2019). Both historical.
CA3
OEM, list or distributor public price
Usually equipment only, not installed.
APC 10 kVA UPS $12,022 reseller. PLC and breaker catalogue prices.
CA4
Marketplace ask, rental, surplus or case study
Calibration only.
Surplus Record 2 MW generator listings.
CA5
Generic estimate or analyst assumption
Engineering allowance only.
Any number without a source scope.
RECONCILIATION ONLY
Aggregate benchmarks (Turner & Townsend, RLB, Arcadis, any $/W or £/MW) sit outside the ladder. They reconcile a total, and never price a component.
Notes: The ontology's evidence taxonomy grades commercial evidence in five levels. Think of it as a ladder where each rung has a job. It also tags evidence along other axes: technical authority, admissibility, whether it is current or historical, and whether it can be normalised. We focus on the commercial ladder because it answers 'how much should I trust this price?'. The top rung, level one, is an executed award, contract, paid schedule or audited actual. It is the strongest because money changed hands. Note the warning on the slide: it may still be a broad package. The Cardonald generator award is a real executed price for a generator with wiring and switchgear, and it does not state the rating, so you cannot turn it into a pounds-per-kW rate. The Southern Water framework lot of four point eight million pounds for UPS supply and install across a region tells you scale and offers no unit rates. Level two is a tender return, a procurement schedule or a formal quantity surveyor's cost plan. Two of the main sources in this course sit here. The EXCOOL cost plan from the second quarter of 2021 and the CIBSE and AECOM cost model from 2019. I class both as level two on my reading of the taxonomy, since each is a formal cost plan or engineering cost model, so treat that classification as mine. The ontology's own label for both is admitted historical. They are strong project-cost evidence for package shape, historical anchors and scaling relationships. Treat both as historical. Level three is an OEM, list or distributor public price. It is usually equipment-only. The small rack UPS price and the PLC catalogue prices are here. Level four is a marketplace ask, a rental, surplus or a case study. The generator listings fall here. It is calibration only. Level five is a generic estimate or analyst assumption. It is an allowance. The dashed box at the bottom matters. Aggregate benchmarks such as the Turner and Townsend cost index, the RLB trends reports and the Arcadis cost reports, plus any dollars per watt figure, are valuable for sanity-checking a total build cost. The ontology limits them to reconciliation. Use them to ask whether a bottom-up sum is plausible, and never to generate a transformer price. A final practical rule. Any number in your model should carry its rung, its date and its scope. If you cannot write those three things next to it, it is not ready to be relied on.

## Slide 30
EVIDENCE | EQUIPMENT PRICE VERSUS INSTALLED COST
Main plant is only about a third of the installed build
Chart: GBP million, Q2 2021, 20 MW
| Direct air | Zero (indirect air) | Fan walls + chillers | Hybrid + chillers (colo) | Hybrid (hyperscale)
Main plant supply (client-procured) | 34.579 | 38.775 | 46.025 | 43.658 | 38.381
Civil, structural, architectural | 20.495 | 20.495 | 23.917 | 24.017 | 24.017
Mechanical installation | 6.029 | 6.075 | 12.533 | 12.697 | 12.022
Electrical installation | 18.122 | 18.561 | 19.647 | 19.9 | 19.375
Support / admin (scope flagged) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
GC preliminaries and OH&P | 13.819 | 13.948 | 16.853 | 16.99 | 16.672
HISTORICAL Q2 2021, LONDON
EXCOOL cost plan | 20 MW | day-1 build | totals £100.5m to £126.5m
32% to 37%
Main plant supply as a share of each scenario total. The rest is civil, installation, support and general contractor cost.
Up to £25.9m
Spread between the cheapest and dearest cooling architecture, about 26% of the lowest case, with the same electrical plant.
£5.0m to £6.3m per MW
Implied by the plan. It reconciles a total. It does not price a component.
Excluded: land, off-site utilities, IT fit-out, fees, finance, VAT and inflation. The £7.5m support line conflicts with the plan's own exclusion note, so it stays flagged.
Notes: This chart is the clearest picture in the course of the gap between an equipment price and an installed cost. It comes from the 2021 EXCOOL cost plan for a twenty-megawatt data centre in London, priced under five different cooling designs. Everything is in millions of pounds in second-quarter 2021 money. The amber block at the bottom of each column is main plant supply, meaning transformers, switchgear, UPS and batteries, generators, chillers and the like, bought directly by the client and supplied to the contractor. Look at its size relative to the total. It is between thirty-two and thirty-seven percent in every scenario. Two-thirds of the cost is something else. Civil, structural and architectural work, mechanical and electrical installation, support and administration space, and the general contractor's preliminaries and overheads and profit. That is the practical meaning of the difference between an equipment price and an installed cost. Take a quote for a generator or a UPS and you have bought the amber block. To get the data centre you add everything else. The cost plan itself lists fifty-two numbered lines, including installation, cabling, containment, builder's work, testing and commissioning. The ontology you have been using describes the equipment. The installation layer is deferred to a separate construction and installation ontology, which we call DR03 later in the course. Second observation. The cooling architecture moves the total by up to about twenty-six million pounds, or twenty-six percent of the lowest case. The fan-wall and chiller case costs more than the direct-air case, in both plant and installation, since it needs chilled-water pipework and chillers. Architecture is a major capex lever, which is why the cooling slides came before this one. Third observation. The implied cost per megawatt in this plan ranges from about five to six point three million pounds. That is a useful benchmark to reconcile a total against. The ontology says plainly that it must not be used to price components. Finally, the box in the bottom right is a reminder of scope. The plan excludes land, off-site utilities, IT fit-out, fees, finance, VAT and construction inflation. It also has an unresolved internal inconsistency. Its notes say office and admin areas are excluded, and the summary includes a seven and a half million pound line for them. The ontology preserves that as an open quality flag. This is a historical anchor with known limits, .

## Slide 31
EVIDENCE | HISTORICAL ANCHORS AND CURRENTISATION
A historical anchor is useful for shape, and a price only after explicit steps
2019
2020
2021
2022
2023
2024
2025
2026
2027
CIBSE/AECOM
2019 cost model
EXCOOL
Q2 2021 cost plan
Model date
2026-10-06
about 5.4 years old, no escalation applied
Five steps between an anchor and a usable estimate
1 Scope
What is in and out? Supply, install, controls, spares
2 Units
kWth, kW IT, kVA, A: align the driver
3 Date
Explicit index input. The workbook leaves it blank
4 Geography
Region, currency, labour market
5 Reconcile
Against current awards, quotes and benchmarks
Output: a currentised estimate, labelled as an estimate. Never relabelled as a price, and never a CA1 or CA3 observation.
The arithmetic of an explicit index
Currentised = anchor x (1 + index change) x scope adjustment x geography factor. Each 10% of escalation moves the £30/kVA transformer anchor by £3/kVA. That is arithmetic only.
What survives age
Ratios inside one cost plan, such as generator rates of £306 to £319 per kW across 2,000 to 3,000 kW, package shape and scope boundaries.
Notes: This slide is the discipline that keeps you from the most common historical-data mistake. Using an old price as if it were today's. The timeline shows two historical anchors. The 2019 CIBSE and AECOM cost model and the second-quarter 2021 EXCOOL cost plan. The model date is early October 2026. The ontology states the EXCOOL plan is about five point four years old, and records that no automatic escalation from 2021 to 2026 has been applied. The escalation factors are left as explicit inputs, deliberately blank. The CIBSE model is older still. The workbook calls these anchors admitted historical. That label has a precise meaning. They are valid evidence in their native scope, and they are never a current price without an explicit currentisation step. The five steps show that currentisation is more than multiplying by an index. First, align scope. A supply-only cost plan line and an installed package are different things. Second, align units. Kilowatts thermal, kilowatts of IT, kVA and amps are different drivers. Third, the date. Choose an index, as an explicit and visible input, with a rationale. Fourth, geography. London in 2021 differs from a mid-sized European market in 2026. Fifth, reconcile the result against current evidence, such as recent awards, fresh quotes and benchmark totals, and see whether it holds up. The output must carry its status. A currentised estimate is an engineering allowance. It should be labelled as one. It must never be re-entered in the model as if it were an observed price, because that would launder a historical number into a current one. The two cards give the arithmetic and the good news. The formula has no hidden pieces. If you assume ten percent escalation, the thirty-pounds-per-kVA transformer anchor moves by three pounds. That arithmetic shows how sensitive the answer is to the index you choose, and forecasts nothing about transformer prices. And the good news is that some things survive age well. Ratios inside one cost plan, such as the generator rate being broadly flat at three hundred and six to three hundred and nineteen pounds per kW across three sizes, tell you about scaling and shape even when the level is out of date.

## Slide 32
EVIDENCE | COMMON MODELLING ERRORS
Eight errors that overstate, understate or falsely sharpen capex
The error
What causes it
The control
1
Parent plus child lines
Genset, UPS and bay quotes already contain children
Apply package controls. Suppress acquisition, keep lifecycle.
2
Housed counted as included
A prefab module houses equipment without pricing it
The vendor bill of materials decides, never the module row.
3
Units swapped
kWth, kW IT, kVA, amps and kW sensible are different drivers
Model each line in its native driver.
4
Historical read as current
EXCOOL is Q2 2021 and CIBSE is 2019
Currentise explicitly and label the result.
5
Equipment treated as installed
Supply-only prices miss install, test and prelims
Add the installation layer (DR03).
6
Benchmark builds components
A $/W figure divided across equipment lines
Benchmarks reconcile totals only.
7
Small price scaled to MW
A 10 kVA retail UPS multiplied up
Match the evidence scale to the line.
8
Observations blended or doubled
List and reseller averaged, or award plus outturn both counted
Keep native observations separate. Count once.
Where the control lives: package controls PKG-001 to PKG-100 in the ontology workbook (sheet 39).
Notes: This is the checklist to use on any model you are handed. Each of these errors is real, and each has a control in the ontology. One, parent plus child lines. If a quote for a generator set, a UPS or a transformer bay already contains its children, adding the children as separate lines double-counts. The package controls handle this case by case and keep children for lifecycle even when they are suppressed for acquisition cost. Two, housed is counted as included. A prefabricated module physically houses equipment. Its price may still exclude it. Only the bill of materials can say. Three, units swapped. Kilowatts thermal, kilowatts of IT, kVA, amps and kilowatts sensible are different drivers. A price per kilowatt thermal applied to kilowatts of IT mixes two quantities that differ by the plant's efficiency. Each line should be modelled in its native driver. Four, historical evidence read as current. The EXCOOL plan is from 2021 and the CIBSE model is from 2019. They need explicit currentisation. Five, equipment treated as installed. We saw that main plant is roughly a third of the installed build in the reference plan. Six, a benchmark used to build components. A dollars-per-watt figure is a total. Dividing it across equipment lines produces numbers that look precise and mean nothing. Seven, a small price scaled to megawatts. A ten kVA retail UPS price is real and current, and it is the wrong scale. Scaling effects, project engineering and bundled scope all change the economics. Eight, observations blended or doubled. The ontology says explicitly not to average a list price and a reseller price, and not to count an award and a later change notice on the same project as independent. For a quick test, take a model and ask three questions of every cost line. What is its driver, and does the unit match the quantity? What is its source rung, date and scope? And what children might already be inside it? If any answer is blank, you have found your next diligence request.

## Slide 33
TRANSACTION USE | RISK MAP BY SYSTEM
Where to spend diligence time: risk differs by system and by dimension
System
Capex weight
Lead time
Double-count risk
Commissioning risk
Lifecycle risk
Current-price gap
HV/MV and transformers
High
High
Medium
Medium
Low
High
Generators and fuel
High
High
High
High
Medium
Medium
UPS and batteries
High
Medium
High
High
High
High
LV, busway, PDU
Medium
Medium
Medium
Medium
Low
Medium
Chillers and hydronics
High
Medium
High
Medium
Medium
High
CRAH, fan wall, IAC
Medium
Medium
Medium
Medium
Medium
High
Direct-to-chip and CDU
High
Medium
High
High
Medium
High
Rear-door and immersion
Medium
Low
Medium
Medium
Medium
High
Fire and life safety
Medium
Low
Low
High
Medium
Medium
Controls, BMS, DCIM
Medium
Low
Medium
High
High
Medium
Fibre and white space
Low
Low
Low
Low
Low
Low
Columns 1 to 5 are analyst judgement for diligence triage, not ontology data. The current-price gap column follows the ontology gap profiles (sheet 14). Ratings describe a typical new-build facility.
Notes: This is a triage map. It tells you where diligence time pays off, system by system. Be clear about what it is. The first five columns are my analyst judgement for a typical new build, intended to focus your questions. Treat them as hypotheses and challenge them. The last column, current-price gap, follows the ontology's gap profiles, which record where public price evidence is weak. Read down the columns. Capex weight is high for the big power and cooling plant: HV and transformers, generators, UPS, chillers and liquid cooling. Fibre and white-space hardware is low. Lead time is highest for the equipment that few factories make at scale, namely HV equipment, transformers and generators. The ontology's benchmark sources, such as the RLB data centre trends reports, give supply-chain context on production-slot pressure. The ontology itself holds no numeric lead times, so none are shown. Double-count risk is highest where package controls exist. Generators, UPS, chillers with pump skids and CDUs. Commissioning risk is highest where integration is heavy. Generators and UPS must prove their handshake, fire systems need witnessed tests, controls need integration testing, and liquid cooling is newer. Lifecycle risk is highest for batteries, which can need up to full string replacement with an interval the ontology marks unknown, and for controls, where obsolescence is different from physical wear. Fire lifecycle is code-driven and the ontology marks it as a gap. The final column is the sobering one. Almost every large system carries a high current-price gap. Generators and controls have some public calibration evidence, and the rest do not. That means the highest-value diligence requests are for quotes, tenders and awards with scope, in exactly the systems that dominate capex. How to use this in practice. Pick the red cells in a target asset's biggest systems. Those are your first diligence requests. Then use the next slide's list to turn each into a specific question and a specific document.

## Slide 34
TRANSACTION USE | DILIGENCE REQUEST LIST
Ten questions that convert the physical system into data-room requests
System | The question that matters | The document that answers it
Grid and HV/MV | Is the MW contracted, energised or deliverable to rack, and who owns the bay? | Connection agreement, energisation certificate, protection study
Transformers | What MVA, what N+x, and what sits inside the quoted package? | Equipment schedule, vendor bill of materials, FAT reports
Generators | How many hours of autonomy at what load, and what do permits allow? | Fuel calculation, emissions permit, load bank report
UPS and batteries | What runtime at today's load, which chemistry, and when are strings replaced? | Discharge test, BMS logs, warranty and replacement plan
LV and busway | Which is the thinnest rating between UPS and rack, against today's density? | Single-line diagrams, thermal imaging, breaker settings
Chillers, room cooling | What capacity at design ambient, with which N+x, and how much spare? | Plant schedule, performance tests, seasonal data
Liquid cooling | Liquid-ready or liquid-installed, and who owns CDUs, fluid and warranty? | Readiness evidence by rung, CDU bill of materials, OEM terms
Fire and safety | Does the authority and insurer accept the current configuration? | Discharge tests, authority certificate, insurer survey
Controls | Who owns licences, configuration and alarm history, and is there one view? | Licence register, point list, alarm logs
Commissioning | Did the integrated test cover the final build, with defects closed? | IST report, snag list, seasonal test record
Notes: Each of these ten rows turns a piece of physical understanding from earlier slides into a request you can put in a data room. Notice that the left column is a system, the middle is a question, and the right is a document. A good diligence request names the document, since that is what lets the seller respond and lets you check the answer. Grid and HV and MV. Ask whether the megawatt is contracted, energised or deliverable to rack, and who owns the bay. The documents are the connection agreement, the energisation certificate and the protection study. Transformers. Ask the MVA, the redundancy, and what is inside the quoted package. The ring main unit, metering and protection are the usual suspects. The documents are the equipment schedule, the vendor bill of materials and the factory test reports. Generators. Ask how many hours of autonomy at what load, and what the permits allow. Running-hour limits and emissions rules can cap value. The documents are the fuel calculation, the permit and the load bank test report. UPS and batteries. Ask runtime at today's load, chemistry and the replacement plan. Request discharge test results, battery management logs, and the warranty. LV and busway. Find the thinnest rating between UPS and rack and compare it with today's density. Request single-line diagrams, thermal imaging and breaker settings. Chillers and room cooling. Ask capacity at design ambient temperature, the redundancy and the spare. Request the plant schedule, the performance test and seasonal data. Liquid cooling. Ask whether the site is liquid-ready or liquid-installed, using the three rungs, and who owns the CDUs, fluid and warranty. Fire and safety. Ask whether the authority and the insurer accept the configuration as it is now. Controls. Ask who owns the licences, configuration and alarm history. Commissioning. Ask whether the integrated systems test covered the final build and whether defects are closed. If you only have time to ask three, ask the grid question, the integrated systems test question and the liquid-readiness question. Between them they cover the three biggest gaps between a claimed megawatt and a usable one.

## Slide 35
TRANSACTION USE | BUY VERSUS BUILD
Replacement cost sets the anchor, and time and risk move it
Main plant supply
34.4%
Installation (mech + elec)
24.0%
Civil, structural, arch.
20.4%
GC prelims and OH&P
13.7%
Support / admin 7.5%
Land, utilities, fees: excluded in source
1 Replacement cost today
Shares: EXCOOL direct-air case, Q2 2021
2 + Time to power and to revenue
3 + Development risk avoided: power, permits, slots
4 - Age and obsolescence: old batteries, air-only design
5 Value anchor
Blocks 2 to 4 are symbolic, not sized. Size each with evidence.
Buy tends to win when
Power is energised and contracted. Capacity is commissioned. Contracts already pay. Supply slots are tight.
Build tends to win when
Power is cheap and available. The design is standard. Customers will wait. You already own the land.
Evidence discipline
The stack gives shape. Total benchmarks reconcile it. Every layer carries a source, date and scope.
Notes: This is where the physical and commercial understanding turns into a transaction view. The question is whether it is better to buy an existing operating asset or to build a new one. Start with column one, replacement cost today. It is the cost to rebuild the capacity from scratch. The stack uses the shares from the 2021 reference cost plan for the direct-air case. Main plant supply is about thirty-four percent. Installation across mechanical and electrical is about twenty-four. Civil, structural and architectural is about twenty. General contractor preliminaries and overheads and profit about fourteen, and support and admin space about seven and a half. The dashed box on top is a reminder that land, off-site utilities and fees are excluded from that source, and they can matter a great deal. Everything in this column is historical and must be currentised before use. Replacement cost is the anchor. Three adjustments move the value of an operating asset away from it. Block two is the time to power and to revenue. A buyer gets capacity today. A builder waits through design, permitting, grid connection, equipment slots, construction and commissioning, and forgoes revenue meanwhile. Block three is the development risk the buyer avoids. Power may not arrive, permits may be refused and supply chains may slip. Block four is the discount for age and obsolescence. Batteries part-way through life, a design that is air-only when customers need liquid cooling, or controls that are near end of support all reduce value relative to new. The floating blocks are symbolic. The point is the structure of the argument, and you should size each block with evidence. The right-hand cards give the heuristic. Buy tends to win when power is energised and contracted, capacity is commissioned, contracts already pay, and supply slots are tight. Build tends to win when power is cheap and available, the design is standard, customers can wait, and the land is already owned. One last discipline. The stack gives shape. A total benchmark such as cost per megawatt reconciles the whole. Every layer you put in the stack needs its source, date and scope, using everything this course has taught about evidence.

## Slide 36
TRANSACTION USE | THE NEXT MODEL LAYER
DR03 adds the installation layer the equipment ontology omits
Equipment ontology
418 lines, branches A to P, quantity drivers, evidence taxonomy
FROZEN v0.1.1
Package controls
Parent and child rules for genset, UPS, transformer bay, prefab modules, pump skids
FROZEN
DR03 construction and installation
Civil, structural, architectural; builder's work; containment and cabling; install labour; prelims and OH&P; testing and commissioning
NEXT LAYER
Outside both layers
Land, off-site utilities, fees, finance, tax
SEPARATE WORK
The cost plan itself separates client-supplied main plant from installation, which is the same seam.
EXCOOL gives DR03 a first skeleton: 52 numbered cost lines
Chart: 
| Civil, structural, architectural | Mechanical installation | Electrical installation | Support / admin | GC prelims and OH&P | Main plant supply
Cost lines | 12 | 12 | 22 | 1 | 2 | 3
What DR03 must capture
Quantity drivers such as floor area, structure volume, metres of containment and cable, and labour. Evidence from QS cost plans, tender bills and executed awards, mapped back to ontology parents.
Q2 2021 line count
Notes: The equipment ontology tells you what physical things exist, how they are packaged and what evidence prices them. It does not tell you what it costs to build the building and install the equipment. That is the job of the next layer, which the workbook calls DR03, the construction and installation ontology. The ontology explicitly defers construction and building fabric to that layer. It does not add them to the equipment list. The four boxes on the left show the layering. First, the equipment ontology: four hundred and eighteen lines in sixteen branches, frozen at version zero point one point one. Second, package controls, which are the parent-and-child rules that prevent double-counting. Also frozen. Third, DR03, the next layer. It will cover civil, structural and architectural work, builder's work, containment and cabling, installation labour, preliminaries and overheads, and testing and commissioning. Fourth, a separate box for things outside both layers. Land, off-site utilities, fees, finance and tax. Why does this layer matter so much? Recall the equipment-versus-installed slide. Main plant was about a third of the build. The other two-thirds sit in layers that the equipment ontology does not cover. The chart shows what the one detailed cost plan we have offers as a skeleton. The EXCOOL plan has fifty-two numbered lines. Twelve are civil, structural and architectural. Twelve are mechanical installation. Twenty-two are electrical installation. One is support space, two are general contractor items and three are main plant supply. The three main plant lines are the ones the equipment ontology covers. The other forty-nine are what DR03 would take on. Because it is one historical cost plan, treat it as a skeleton to be completed with more sources. The card on the right lists what DR03 must capture. Quantity drivers such as floor area, structural volume, metres of containment and cable, and labour hours. And evidence from cost plans, tender bills and awards, each mapped back to the ontology parent it installs. When that exists, the bottom-up model can be reconciled in full against a total benchmark.

## Slide 37
THE FIVE-MOVE TEST
Apply it to any line in any model
1
Job
What physical job does it do?
2
Driver
What sets its size or count?
3
Package
What else is inside the price?
4
Evidence
Which rung, date and scope?
5
Risk
What can fail commercially?
Worked example: a CDU quote lands in the data room
Isolates and exchanges heat between rack and facility loops
kWth or racks, with N+1 pumps or units
Pumps, exchanger, filters, controls may or may not be inside
Quote or tender with scope. No current public price
Boundary, leak and warranty ownership, lead time
Know the chain.
Power in, heat out, assurance around.
Know the package.
Included, housed, installed and commissioned differ.
Know the date.
Historical evidence is shape until it is currentised.
Notes: Let us end with the framework you can carry into any transaction. Five moves, applied to any line in any model. Move one, job. What physical job does this item do, and what happens if it is missing? If you cannot say it in a sentence, you still need to study the line. Move two, driver. What sets its size or its count? Megavolt-amps, kilowatts, kilowatts thermal, runtime, rack count, metres, amps or litres. If the unit of the price does not match the unit of the quantity, the line is wrong. Move three, package. What else is inside the price, and what is outside it? Remember the four states: included, housed, installed and commissioned. Move four, evidence. Which rung of the ladder, which date and which scope? Executed award, cost plan, list price, marketplace ask or assumption. Current or historical. Package or component. Move five, risk. What can go wrong commercially? Capex, lead time, double-counting, commissioning, lifecycle replacement, customer acceptance or bankability. The worked example applies it to a CDU quote arriving in a data room. The job is to isolate and exchange heat between the rack loop and the facility loop. The driver is kilowatts thermal or racks, with redundancy. The package is uncertain. Pumps, heat exchanger, filters and controls may or may not be inside, and no frozen rule settles it, so you ask for the bill of materials. The evidence is a quote or tender with scope, because there is no current public price. The risks are the boundary of scope, leak and warranty ownership, and lead time. In five moves you have turned a vague line into five specific diligence requests. Finally, three rules to take away. Know the chain: power in, heat out, assurance around. Know the package: included, housed, installed and commissioned are different. Know the date: historical evidence is shape until it is explicitly currentised. If you apply those, you will find the errors that other people miss, you will ask for the documents that matter, and you will be honest about the numbers that nobody can defend today. Thank you.